## Input
Project Number : |  | KXEO - 00045 / 66-6705-700 |  |  |  |  | Input Date : | 2018-04-06
Construction Unit : | [6 empty] | Equipment No./ Civil Item No.:
Prep By/Checked By : | [6 empty] | Revision Status :
Title : DESIGN OF RAFT FOUNDATION AS PER BS EN1992-1-1:2010
SHEET -1
A | DEFAULT VALUES |  | (As per PDE-CVC-G00-EB-0002)
A.1 | Exposure class for No risk |  |  |  |  | X0 | For concrete without reinforcement or embedded metal, all exposures
| Exposure class Carbonation-induced corrosion |  |  |  |  | XC4 | Cyclic wet and dry
| Exposure class for Chloride-induced corrosion |  |  |  |  | XD1 | Moderate humidity
| Exposure class for Chloride-induced corrosion from sea-watert |  |  |  |  | XS1 | Exposed to airborne salt but not in direct contact with sea water
| Exposure class for Freeze/Thaw Attack |  |  |  |  | XF1 | Moderate water saturation, without de-icing agent
| Exposure class for Chemical Attack |  |  |  |  | XA1 | Slightly aggressive chemical environment according to EN 206-1, Table 2
(Table 4.1, EN1992-1-1:2010 )
| Service Life |  |  |  |  | 100 | years
| Structural class for pilecap design |  |  |  |  | S4
( Assuming Air entrainment < 4 % , Good Quanility control at site ,Nominal size of Aggregates <32mm)
| Maximum permissible crack width |  |  |  |  | 0.3 | mm | (Table 7.1N ,BS EN1992-1-1:2010)
A.2 | Grade of structural concrete |  |  |  |  | C30/37 |  |  | AS per PDE-CVC-G00-EB-0002
| fck = Characteristics compressive cylindrical strength |  |  |  |  | 30 | N/mm2 | (Table 3.1,EN1992-1-1:2010)
| fctm = |  |  |  |  | 2.9 | N/mm2
| Grade of lean concrete |  |  |  | = | C12/15
| Reinforcment ,Yield Strength , fyk |  |  |  | = | 500 | N/mm2
[5 empty] | = | 434.7826 | N/mm2
(Table C.1 BS EN1992-1-1:2010 Annex C)
| Unit wt. of Concrete (wc) |  |  |  | = | 25 | kN/m3
| Thickness of lean concrete (tl) |  |  |  | = | 50
| Soil depth to be ignored as overburden (dts) |  |  |  | = | 0
| Concrete clear cover to main reinf. (Top & Side) in pilecap(Ct) |  |  |  | = | 35 |  | (cl. 4.4.1,BS EN1992-1-1:2010)
| Y = Pile anchorage into pile cap |  |  |  | = | 50 |  |  | PDE-CVC-G00-ED-0001
| Clear cover to main reinf. (Bottom) in pile cap (Cb) |  |  |  |  | 50 |  | (cl. 4.4.1, EN1992-1-1:2010) |  | OK
(Bottom Nominal cover Cb = pile anchorage (Y) in to pile cap + No clearance assumed)
A.4 | fcm = fck + 8 |  |  |  | = | 38 | N/mm2 | (Table 3.1,EN1992-1-1:2010)
| Modulus of Elasticity for concrete, Ecm = 22*[fcm /10]0.3 |  |  |  | = | 32.8366 | N/mm2
| Modulus of Elasticity for Reinforcement, Es |  |  |  | = | 200000 | N/mm2 | (cl. 3.2.7 (4),EN1992-1-1:2010)
A.5 | Partial factor for materials for ultimate limit states
| For concrete |  |  | gc | = | 1.5 | (cl. 2.4.2.4 EN1992-1-1:2010 and National Annex)
| For reinforcement steel |  |  | gs | = | 1.15
A.6 | Seismic Parameters as per EUROCODE & Project design basis
Design seismic coefficient is assumed on higher side
| Coefficient required to be multiplyed with mass to get base shear , Sd(T) |  |  |  | = | 0.1
( design seismic response coefficient, is required to calculate the sesmic force due to selfweight of pilecap)
B | PLATE RESULTS
| MAX Mx = |  |  |  |  | 2199.705 | kN-m/m | FROM StaadPro Analysis
| MIN Mx = |  |  |  |  | -1030.131 | kN-m/m
| MAX My = |  |  |  |  | 2518.246 | kN-m/m
| MIN My = |  |  |  |  | -2414.616 | kN-m/m
C | ANCHOR BOLT DETAILS
| Type of anchor bolts(As per Engineering spec. or design basis) |  |  |  | = | A
| Diameter (Db) |  |  |  | = | 100
| No. of bolts (Nb) |  |  |  | = | 36
| Embedment length in concrete |  |  |  | = | 970 | mm | PDE-CVC-G00-EC-0004
| Thickness of grout (tg) |  |  |  | = | 30 | mm
| Yield stress of Bolts, Fyb |  |  |  | = | 240 | N/mm2
| Civil Design Basis no. |  |  |  |  | XXXX-CI-DOC-0001
| Concept Note no. |  |  |  |  | ---
| Height of Equipment |  |  |  |  | 20 | m
D | RAFT DETAILS |  | ( Top of raft is considred at Ground Level )
| Top Of Grout (TOG) Elevation EL |  |  | EL | = | 100.2 | m
| Ground level to be considered for Excavation EL |  |  | EL | = | 100 | m
| D = Depth of raft (from TOG to Bottom of raft) |  |  |  | = | 2170 | mm
| Effective depth "d" = (dy+dz)/2 |  |  |  | = | 2100 | mm
| Under Side of raft |  |  | EL | = | 98 | m
| Length of Raft "L" |  |  |  | = | 20.5 | m
| Width of Raft "B" |  |  |  | = | 12 | m
E | PILE DETAILS
| Area as per soil report |  |  |  |  | IV
| Pile Spacing = |  |  |  |  | 4d
| Diameter of Pile Dp = |  |  |  |  | 500 | mm
| Length of Pile Lp = |  |  |  |  | 19.1 | m
| Type of Pile based on Connectors = |  |  |  |  | Type II
| Design Compression Capacity of pile = |  |  |  |  | 1950 | kN
| Design Tension Capacity of pile = |  |  |  |  | 374.36 | kN
| No of Piles provide = |  |  |  |  | 75
Nb= (π2𝐸_cm Iz)/(klu)2
δsz=1/(1−𝑃_𝑢𝑝/𝑁_𝑏 )

## Pile Reaction Check
Project Number : |  | KXEO - 00045 / 66-6705-700 | [5 empty] | Input Date : | 2018-04-06
Construction Unit : | [7 empty] | Equipment No./ Civil Item No.:
Prep By/Checked By : | [7 empty] | Revision Status :
Title : DESIGN OF RAFT FOUNDATION AS PER BS EN1992-1-1:2010
SHEET -2
Paste support reaction from staad :
|  |  | Horizontal | Vertical | Horizontal | Moment
| Node | L/C | Fx kN | Fy kN | Fz kN | Mx kN-m | My kN-m | Mz kN-m
Max Fx | 129 | 2002 0.9D+1.5WL+0.9TS+1.5I | 17.695 | 321.231 | -5.343 | 0 | -0.02 | 0 |  |  | 321.231 | 17.695 | 5.343 |  | 18.484 | 321.231
Min Fx | 64 | 2401 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -29.962 | 294.933 | -25.948 | 0 | -0.065 | 0 |  |  | 294.933 | 29.962 | 25.948 |  | 39.636 | 294.933
Max Fy | 206 | 2404 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -10.568 | 760.694 | -7.933 | 0 | 0.193 | 0 |  |  | 760.694 | 10.568 | 7.933
Min Fy | 216 | 2012 0.9D+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -10.355 | -143.017 | -4.315 | 0 | -0.169 | 0 |  |  | -143.017 | 10.355 | 4.315
Max Fz | 176 | 2004 0.9D+1.5WL+0.9TS+1.5I | -1.051 | 35.302 | 13.454 | 0 | -0.037 | 0 |  |  | 35.302 | 1.051 | 13.454 |  | 13.495 | 35.302
Min Fz | 161 | 2403 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -10.955 | 399.308 | -44.941 | 0 | -0.084 | 0 |  |  | 399.308 | 10.955 | 44.941 |  | 46.257 | 399.308
Max Mx | 35 | 2001 0.9D+1.5WL+0.9TS+1.5I | -19.449 | 167.276 | -5.34 | 0 | 0.022 | 0 |  |  | 167.276 | 19.449 | 5.34
Min Mx | 35 | 2001 0.9D+1.5WL+0.9TS+1.5I | -19.449 | 167.276 | -5.34 | 0 | 0.022 | 0 |  |  | 167.276 | 19.449 | 5.34
Max My | 226 | 2401 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -28.964 | 173.118 | -25.554 | 0 | 0.809 | 0 |  |  | 173.118 | 28.964 | 25.554
Min My | 196 | 2401 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -29.761 | 555.471 | -26.349 | 0 | -0.991 | 0 |  |  | 555.471 | 29.761 | 26.349
Max Mz | 35 | 2001 0.9D+1.5WL+0.9TS+1.5I | -19.449 | 167.276 | -5.34 | 0 | 0.022 | 0 |  |  | 167.276 | 19.449 | 5.34
Min Mz | 35 | 2001 0.9D+1.5WL+0.9TS+1.5I | -19.449 | 167.276 | -5.34 | 0 | 0.022 | 0 |  |  | 167.276 | 19.449 | 5.34
[11 empty] | -143.017 | 10.355 | 4.315 | 11.218
Case I : Maximum Compression
|  | Maximum compression = |  | 760.694 | kN
|  | Corresponding shear in X = |  | 10.568 | kN
|  | Corresponding shear in Z = |  | 7.933 | kN
|  | Resultant Shear = |  | 13.214 | kN
Case II : Maximum Tension
|  | Maximum Tension = |  | -143.017 | kN | [5 empty] | 10.355
|  | Corresponding shear in X = |  | 10.355 | kN | [5 empty] | 4.315
|  | Corresponding shear in Z = |  | 4.315 | kN
|  | Resultant Shar = |  | 11.218 | kN | [5 empty] | 17.695 | 321.231
| Case III : Maximum Shear | [9 empty] | 29.962 | 294.933
|  | Maximum Resultant shear case A = |  | 39.636 | kN | [5 empty] | 10.568 | 760.694
|  | Corresponding vertical load = |  | 294.933 | kN | [5 empty] | 10.355 | -143.017
|  | Maximum Resultant shear case B = |  | 46.257 | kN | [5 empty] | 1.051 | 35.302
|  | Corresponding vertical load = |  | 399.308 | kN | [5 empty] | 10.955 | 399.308
[11 empty] | 19.449 | 167.276
| Buoyancy force per pile = (L x B x D x 10 / number of piles ) |  |  | -71.176 | kN | [5 empty] | 19.449 | 167.276
[11 empty] | 28.964 | 173.118
[11 empty] | 29.761 | 555.471
| Pile capacity check for Case I | [9 empty] | 19.449 | 167.276
|  | Total Compression = Maximum compression - Buoyancy force = |  | 689.518 | kN | [5 empty] | 19.449 | 167.276
|  | Ultimalte Shear Capacity of pile corresponding to actual compression = |  | 82.3709 | kN
[11 empty] | 5.343 | 321.231
|  | Utility ratio for Pile compression = |  | 0.3901 | < 1 ,OK | [5 empty] | 25.948 | 294.933
|  | Utility ratio for Pile shear = |  | 0.16042 | < 1 ,OK | [5 empty] | 7.933 | 760.694
[11 empty] | 4.315 | -143.017
[11 empty] | 13.454 | 35.302
| Pile capacity check for Case II | [9 empty] | 44.941 | 399.308
[11 empty] | 5.34 | 167.276
|  | Total tension = Tension force + Buoyancy force |  | -214.193 | kN | [5 empty] | 5.34 | 167.276
|  | Ultimalte Shear Capacity of pile corresponding to actual tension = |  | 27.0065 | kN | [5 empty] | 25.554 | 173.118
[11 empty] | 26.349 | 555.471
|  | Utility ratio for Pile tension = |  | 0.57216 | < 1 ,OK | [5 empty] | 5.34 | 167.276
|  | Utility ratio for Pile shear = |  | 0.41538 | < 1 ,OK | [5 empty] | 5.34 | 167.276
Pile capacity check for Case III
|  | Ultimalte Shear Capacity of pile corresponding to actual vertical load for case A = |  | 63.3284 | kN
|  | Utility ratio for Pile shear = |  | 0.62588 | < 1 ,OK
|  | Ultimalte Shear Capacity of pile corresponding to actual vertical load for case B = |  | 71.0599 | kN
|  | Utility ratio for Pile shear = |  | 0.65096 | < 1 ,OK

## Staad Stress Resulsts
STAAD analysis results for Flexure
|  |  | Shear |  | Membrane |  |  | Bending Moment |  |  | Wood-Armer Moments
| Plate | L/C | SQX (local) N/mm2 | SQY (local) N/mm2 | SX (local) N/mm2 | SY (local) N/mm2 | SXY (local) N/mm2 | Mx kN-m/m | My kN-m/m | Mxy kN-m/m | Mx + Mxy | Mx - Mxy | My + Mxy | My - Mxy
Max Qx | 541 | 2601 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 1.042 | -0.196 | -0.032 | 0 | 0.005 | -106.444 | -130.333 | 457.629 | 351.185 | -564.073 | 327.296 | -587.962
Min Qx | 541 | 2602 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -1.172 | 0.306 | 0.03 | 0 | -0.005 | 964.664 | 145.418 | -482.114 | 482.55 | 1446.778 | -336.696 | 627.532
Max Qy | 524 | 2602 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.623 | 1.422 | 0.026 | 0.049 | -0.018 | -39.927 | 2513.065 | 5.181 | -34.746 | -45.108 | 2518.246 | 2507.884
Min Qy | 524 | 2601 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.58 | -1.209 | -0.027 | -0.05 | 0.019 | 151.32 | -2411.985 | -2.631 | 148.689 | 153.951 | -2414.616 | -2409.354
Max Sx | 928 | 2601 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.218 | -0.107 | 0.048 | -0.003 | 0 | 1089.575 | 38.58 | 46.626 | 1136.201 | 1042.949 | 85.206 | -8.046
Min Sx | 928 | 2602 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.035 | 0.045 | -0.048 | 0.003 | 0 | -268.704 | -27.46 | -63.132 | -331.836 | -205.572 | -90.592 | 35.672
Max Sy | 524 | 2007 0.9D+1.5WL+0.9TS+1.5I | 0.142 | -0.317 | 0.019 | 0.091 | -0.014 | 154.786 | 570.316 | -173.038 | -18.252 | 327.824 | 397.278 | 743.354
Min Sy | 524 | 2404 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -0.186 | 0.519 | -0.02 | -0.093 | 0.015 | -48.023 | -494.016 | 173.145 | 125.122 | -221.168 | -320.871 | -667.161
Max Sxy | 87 | 2604 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.199 | 0.4 | -0.01 | 0.006 | 0.036 | 1367.386 | 530.404 | -415.521 | 951.865 | 1782.907 | 114.883 | 945.925
Min Sxy | 87 | 2603 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.325 | -0.06 | 0.01 | -0.006 | -0.036 | 76.476 | 299.679 | 520.091 | 596.567 | -443.615 | 819.77 | -220.412
Max Mx | 170 | 2604 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.329 | 0.141 | 0.012 | 0.007 | 0.004 | 2117.8 | 1467.706 | -81.905 | 2035.895 | 2199.705 | 1385.801 | 1549.611
Min Mx | 191 | 2603 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.387 | -0.031 | 0.028 | -0.001 | 0 | -1014.155 | -185.007 | -15.976 | -1030.131 | -998.179 | -200.983 | -169.031
Max My | 524 | 2602 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.623 | 1.422 | 0.026 | 0.049 | -0.018 | -39.927 | 2513.065 | 5.181 | -34.746 | -45.108 | 2518.246 | 2507.884
Min My | 524 | 2601 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.58 | -1.209 | -0.027 | -0.05 | 0.019 | 151.32 | -2411.985 | -2.631 | 148.689 | 153.951 | -2414.616 | -2409.354
Max Mxy | 583 | 2601 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.146 | 0.143 | -0.017 | -0.014 | 0.013 | 399.347 | -969.319 | 1246.705 | 1646.052 | -847.358 | 277.386 | -2216.024
Min Mxy | 582 | 2602 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.131 | -0.115 | 0.02 | 0.021 | -0.018 | 598.473 | 919.219 | -1267.572 | -669.099 | 1866.045 | -348.353 | 2186.791
[11 empty] | 2035.895 | 2199.705 | 2518.246 | 2507.884
[11 empty] | -1030.131 | -998.179 | -2414.616 | -2409.354
STAAD analysis results for shear check (AT A DISTANCE OF "d" FROM FACE OF COLUMN & PILE)
|  |  | Shear |  | Membrane |  |  | Bending Moment |  |  | Wood-Armer Moments
| Plate | L/C | SQX (local) N/mm2 | SQY (local) N/mm2 | SX (local) N/mm2 | SY (local) N/mm2 | SXY (local) N/mm2 | Mx kN-m/m | My kN-m/m | Mxy kN-m/m | Mx + Mxy | Mx - Mxy | My + Mxy | My - Mxy | 839.79 | KN
Max Qx | 907 | 2604 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.35 | -0.11 | -0.018 | 0 | -0.001 | 266.619 | -33.426 | 108.247 | 374.866 | 158.372 | 74.821 | -141.673
Min Qx | 818 | 2601 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.387 | 0 | 0.028 | -0.001 | -0.003 | 143.369 | -0.741 | 181.666 | 325.035 | -38.297 | 180.925 | -182.407 | 0.35 | 0.11
Max Qy | 430 | 2010 0.9D+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | 0.054 | 0.361 | -0.002 | -0.011 | 0.003 | 657.615 | 745.211 | 294.799 | 952.414 | 362.816 | 1040.01 | 450.412 | 0.387 | 0
Min Qy | 301 | 2603 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | 0.127 | -0.336 | -0.012 | 0.008 | 0.017 | 765.056 | 522.087 | -206.438 | 558.618 | 971.494 | 315.649 | 728.525 | 0.054 | 0.361
Max Sx | 818 | 2405 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -0.306 | -0.008 | 0.029 | -0.001 | -0.003 | 286.183 | 4.044 | 133.754 | 419.937 | 152.429 | 137.798 | -129.71 | 0.127 | 0.336
Min Sx | 818 | 2002 0.9D+1.5WL+0.9TS+1.5I | 0.259 | -0.007 | -0.029 | 0.001 | 0.003 | 83.465 | 6.283 | -141.796 | -58.331 | 225.261 | -135.513 | 148.079 | 0.306 | 0.008
Max Sy | 453 | 2405 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | 0.114 | -0.07 | -0.002 | 0.031 | -0.005 | 158.302 | -826.808 | -150.731 | 7.571 | 309.033 | -977.539 | -676.077 | 0.259 | 0.007
Min Sy | 453 | 2002 0.9D+1.5WL+0.9TS+1.5I | -0.203 | 0.103 | 0.002 | -0.03 | 0.005 | 190.252 | 827.551 | 146.464 | 336.716 | 43.788 | 974.015 | 681.087 | 0.114 | 0.07
Max Sxy | 431 | 2404 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | 0.091 | 0.062 | -0.001 | 0.009 | 0.023 | 527.461 | -292.736 | -103.389 | 424.072 | 630.85 | -396.125 | -189.347 | 0.203 | 0.103
Min Sxy | 431 | 2007 0.9D+1.5WL+0.9TS+1.5I | -0.106 | -0.023 | 0.001 | -0.009 | -0.023 | -18.342 | 208.837 | 99.136 | 80.794 | -117.478 | 307.973 | 109.701 | 0.091 | 0.062
Max Mx | 907 | 2405 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | 0.132 | 0.103 | 0.006 | 0.011 | -0.001 | 1075.352 | 466.21 | 35.132 | 1110.484 | 1040.22 | 501.342 | 431.078 | 0.106 | 0.023
Min Mx | 568 | 2002 0.9D+1.5WL+0.9TS+1.5I | -0.025 | -0.245 | 0.014 | -0.001 | 0.015 | -432.621 | 540.406 | 34.904 | -397.717 | -467.525 | 575.31 | 505.502 | 0.132 | 0.103
Max My | 548 | 2602 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.077 | -0.066 | 0.013 | 0.002 | 0.011 | -285.9 | 1172.29 | 132.475 | -153.425 | -418.375 | 1304.765 | 1039.815 | 0.025 | 0.245
Min My | 449 | 2405 1.35D+1.2LL+1.35OLE+1.35AL+1.5WL+0.9TS+1.5I | -0.018 | -0.013 | -0.001 | -0.005 | 0.002 | 178.823 | -1036.582 | -335.733 | -156.91 | 514.556 | -1372.315 | -700.849 | 0.077 | 0.066
Max Mxy | 668 | 2601 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.031 | 0.036 | 0.002 | -0.004 | -0.022 | 378.001 | -355.401 | 657.024 | 1035.025 | -279.023 | 301.623 | -1012.425 | 0.018 | 0.013
Min Mxy | 708 | 2602 1.0D+0.15LL+0.8OLE+0.8AL+1.0SES+1.0I | -0.012 | -0.044 | -0.007 | 0.007 | 0.02 | 58.343 | 431.107 | -590.396 | -532.053 | 648.739 | -159.289 | 1021.503 | 0.031 | 0.036
[11 empty] | 1110.484 | 1040.22 | 1304.765 | 1039.815 | 0.012 | 0.044
[11 empty] | -532.053 | -467.525 | -1372.315 | -1012.425
STAAD analysis results for crack width calculation (Use working load cases)
|  |  | Shear |  | Membrane |  |  | Bending Moment |  |  | Wood-Armer Moments
| Plate | L/C | SQX (local) N/mm2 | SQY (local) N/mm2 | SX (local) N/mm2 | SY (local) N/mm2 | SXY (local) N/mm2 | Mx kN-m/m | My kN-m/m | Mxy kN-m/m | Mx + Mxy | Mx - Mxy | My + Mxy | My - Mxy
Max Qx | 541 | 1901 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.457 | -0.065 | -0.021 | 0 | 0.004 | 168.894 | -56.031 | 204.038 | 372.932 | -35.144 | 148.007 | -260.069
Min Qx | 541 | 1902 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | -0.586 | 0.175 | 0.02 | 0 | -0.004 | 692.281 | 71.121 | -228.007 | 464.274 | 920.288 | -156.886 | 299.128
Max Qy | 524 | 1902 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | -0.302 | 0.7 | 0.024 | 0.049 | -0.02 | -16.509 | 1196.731 | 56.782 | 40.273 | -73.291 | 1253.513 | 1139.949
Min Qy | 524 | 1901 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.26 | -0.488 | -0.025 | -0.05 | 0.02 | 129.124 | -1097.295 | -55.161 | 73.963 | 184.285 | -1152.456 | -1042.134
Max Sx | 544 | 1902 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | -0.431 | 0.297 | 0.03 | 0.031 | -0.008 | -166.301 | 1033.053 | -150.747 | -317.048 | -15.554 | 882.306 | 1183.8
Min Sx | 544 | 1901 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.335 | -0.136 | -0.03 | -0.032 | 0.008 | 470.942 | -902.673 | 177.763 | 648.705 | 293.179 | -724.91 | -1080.436
Max Sy | 524 | 1903 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.086 | -0.151 | 0.012 | 0.061 | -0.009 | 146.418 | 400.538 | -117.48 | 28.938 | 263.898 | 283.058 | 518.018
Min Sy | 524 | 1904 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | -0.128 | 0.362 | -0.013 | -0.062 | 0.01 | -33.799 | -301.114 | 119.099 | 85.3 | -152.898 | -182.015 | -420.213
Max Sxy | 87 | 1904 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.046 | 0.267 | -0.005 | 0.003 | 0.021 | 978.833 | 464.781 | -172.376 | 806.457 | 1151.209 | 292.405 | 637.157
Min Sxy | 87 | 1903 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | -0.172 | 0.073 | 0.005 | -0.003 | -0.021 | 464.957 | 365.324 | 276.875 | 741.832 | 188.082 | 642.199 | 88.449
Max Mx | 186 | 1825 1.0D+0.15LL+1.0HT+1.0AL+1.0TS+1.0I | -0.014 | 0.022 | 0 | 0 | 0 | 1448.853 | 1433.698 | 15.727 | 1464.58 | 1433.126 | 1449.425 | 1417.971
Min Mx | 706 | 1903 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.1 | 0.015 | 0.01 | 0.006 | 0.007 | -202.999 | -54.477 | -88.191 | -291.19 | -114.808 | -142.668 | 33.714
Max My | 186 | 1830 1.0D+0.15LL+1.0HT+1.0AL+1.0TS+1.0I | -0.014 | 0.022 | 0 | 0 | 0 | 1448.665 | 1433.793 | 15.575 | 1464.24 | 1433.09 | 1449.368 | 1418.218
Min My | 524 | 1901 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.26 | -0.488 | -0.025 | -0.05 | 0.02 | 129.124 | -1097.295 | -55.161 | 73.963 | 184.285 | -1152.456 | -1042.134
Max Mxy | 583 | 1901 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | 0.048 | 0.114 | -0.012 | -0.016 | 0.013 | 356.293 | -320.272 | 573.099 | 929.392 | -216.806 | 252.827 | -893.371
Min Mxy | 582 | 1902 1.0D+0.15LL+0.8OLE+0.8AL+1.0W+1.0I | -0.105 | -0.021 | 0.015 | 0.016 | -0.015 | 487.164 | 483.526 | -589.396 | -102.232 | 1076.56 | -105.87 | 1072.922
[11 empty] | 1464.58 | 1433.126 | 1449.425 | 1418.218
[11 empty] | -317.048 | -216.806 | -1152.456 | -1080.436

## Flexure
Master File Name : | [6 empty] | Input Date :
Project Number : | [6 empty] | Proj. Related settings by LE on :
Project Std. File Name : | [6 empty] | Unit / Equipment No.:
Prep By/Checked By : | [6 empty] | Revision Status :
Title :
NOTE: USER TO ENTER DATA IN CELLS WITH PALE BLUE BACKGROUND AND LE TO
CONFIRM VALUES IN CELLS WITH YELLOW BACKGROUND.
Derivation to find dreq :
Fig. 3.5 Rectangular Stress distribution (Cl. 3.1.7, EN 1992-1-1)
Assuming fck ≤ 50 Mpa
| η = 1 for fck ≤ 50 |  |  |  | λ = 0.8 for fck ≤ 50
The x/d ratio can be written in terms of the steel strain as illustrated in Figure.
Lever Arm distance |  | z
Bending of the section (according to Figure 3.5) will induce a resultant tensile force, Fs in the reinforcing steel, and a resultant compressive force in the concrete Fc which acts through the centroid of the effective compressed area .
For equilibrium, the ULS design moment MEd has to be balanced by the resisting moment MRd so that:
Where, z is the lever arm between the resultant forces Fc & Fs.
or
where
Rearranging,
or
These equations are valid under the assumption that the reinforcing steel yields before the concrete crushes.
The corresponding compression force is
whereas the inner lever arm is:
For Limiting Moment of Resistance
| xbal/d = | 0.45
| zbal/d = | 0.82
| Kbal = | 0.2952
Hence, the expression for depth required for balance section, dreq
| dreq = | 867.33 | mm | < | dprovided | OK
Check for under-reinforced section:
For under-reinforced section
| K = | 0.0285 |  | OK
Derivation to find Ast:
Referring to the figure above
Total Tensile Force, Fs
Also, Moment is equal to Force multiplied by lever arm distance, z
Rearranging, we get
Minimum Reinforcement
Minimum reinforcement in each direction = |  |  |  | 0.0015bt |  | 1575 | mm2 | 9.2.1.1 of EN1992
TOP REINFORCEMENT (BOTTOM)
Reinforcement in X direction (Mx +ve)
Ast required | [5 empty] | 2444.5466 | mm2
Dia of bar in X direction | [5 empty] | 20 | mm
Spacing provided in X direction | [5 empty] | 100 | mm
Ast provided in X direction | [5 empty] | 3142.8571 | mm2
OK
BOTTOM REINFORCEMENT (TOP)
Reinforcement in X direction (Mx -ve)
Ast required | [5 empty] | 1144.7913 | mm2
Dia of bar in X direction | [5 empty] | 20 | mm
Spacing provided in X direction | [5 empty] | 100 | mm
Ast provided in X direction | [5 empty] | 3142.8571 | mm2
OK
TOP REINFORCEMENT (BOTTOM)
Reinforcement in Y direction (My +ve)
Ast required | [5 empty] | 2798.5433 | mm2
Dia of bar in Y direction | [5 empty] | 20 | mm
Spacing provided in Y direction | [5 empty] | 100 | mm
Ast provided in Y direction | [5 empty] | 3142.8571 | mm2
OK
BOTTOM REINFORCEMENT (TOP)
Reinforcement in Y direction (My -ve)
Ast required | [5 empty] | 2683.3786 | mm2
Dia of bar in X direction | [5 empty] | 20 | mm
Spacing provided in X direction | [5 empty] | 100 | mm
Ast provided in X direction | [5 empty] | 3142.8571 | mm2
OK
𝑥/𝑑=ϵ𝑐𝑢3/(ϵ𝑐𝑢3+ϵ𝑠)
𝜖_𝑠=0.002+𝑓_𝑦𝑘/((ϒ_𝑠∗𝐸_𝑠))
"z = d−" 𝜆𝑥/2 " "
𝑀_𝑏𝑎𝑙=𝑓_𝑐𝑑 𝑏𝑑^2 (1−𝑧_𝑏𝑎𝑙/𝑑) 𝑧_𝑏𝑎𝑙/𝑑∗2
𝐾_𝑏𝑎𝑙=𝑀_𝑏𝑎𝑙/𝑓_𝑐𝑑 𝑏𝑑^2
𝑑_𝑟𝑒𝑞=√(𝑀/(〖𝐾_𝑏𝑎𝑙 𝑓〗_𝑐𝑑 𝑏))
𝐹_𝑠=0.87𝑓_𝑦𝑘 𝐴_𝑠𝑡
𝑀=0.87𝑓_𝑦𝑘 𝐴_𝑠𝑡∗𝑧
𝐴_𝑠𝑡=𝑀/(0.87𝑓_𝑦𝑘 ∗𝑧)
𝜖_𝑐𝑢3=0.0035
𝑀_𝐸𝑑=𝐹_𝑐 𝑧=𝐹_𝑠 𝑧
𝐹_𝑐=𝑓_𝑐𝑑 𝑏𝑥
𝑀_𝐸𝑑=𝑓_𝑐𝑑 𝑏𝑑^2 (1−𝑧/𝑑) 𝑧/𝑑∗2
𝑀_𝐸𝑑/(𝑓_𝑐𝑑 𝑏𝑑^2 )=𝐾
𝐾=(1−𝑧/𝑑) 𝑧/𝑑∗2
𝑧/𝑑=0.5+√(0.25−0.5𝐾)
𝑧/𝑑=0.5(1+√(1−2𝐾))
𝐹_(𝑐,𝑏𝑎𝑙)=𝑓_𝑐𝑑 𝑏𝑥=𝑓_𝑐𝑑 𝑏∗0.8∗0.45𝑑
𝑧_𝑏𝑎𝑙=𝑑−((0.8∗0.45𝑑))/2=0.82𝑑
𝐾<𝐾_𝑏𝑎𝑙

## Punching Shear
For Piles
Check for Punching shear resistance of column bases without shear reinforcement
As per clause 6.4.4 (2) EN 1992-1-1 ed 11
The punching shear resistance should be verified at control perimeters within 2d
from the periphery of the column, so we have considered critical section at d from face of pile
where
fck | = | 30 | Mpa |  | Pile dia. | = | 500 | mm
Average effective depth,
deff | = | 2100 | mm
a | = | d | mm (max 2d) |  | a is the distance from the periphery of the column
| = | 2100 | mm |  | to the control perimeter considered
Refer CL. 6.4.4 (2) EN 1992-1-1 ed 11
k | = | 1.3086 | ≤ 2
CRd,c | = | 0.18/γc |  |  | γc | = | 1.5 | (refer Table 2.1N, EN 1992-1-1)
CRd,c | = | 0.12 |  |  | Refer Cl. 6.4.4(1) note (EN 1992 1-1)
vmin | = | 0.035 k3/2 fck1/2 |  |  | Refer EQ. 6.3N (EN 1992 1-1)
vmin | = | 0.28697
bw | is the smallest width of the c/s in the tensile area (mm)
bw | = | 1000 | mm
ᵨlx | = | 0.0014966
ᵨlz | = | 0.0014966
ᵨl = sqrt(ᵨlx * ᵨlz) = |  | 0.0014966 | ≤ 0.02
vRd | = | 0.51786 | N/mm2
vRd, min | = | 0.57395 | N/mm2
vRd, max | = | 0.4 v fcd |  |  | Refer Note of Clause 6.4.5(3) (EN 1992 1-1)
Strength reduction factor for concrete cracked in shear
Refer EQ. 6.6N (EN 1992 1-1)
v | = | 0.528
αcc | = | 0.85
fcd | = | αcc fck / γc | = | 17 | Refer EQ. 3.15 (EN 1992 1-1)
vRd, max | = | 3.5904 | N/mm2
Actual shear stress Ved = |  |  | 0.387 | N/mm2
Ok, safe in Shear
For concentric loading the net applied force is
VEd,red | = | VEd - ∆ VEd
where
VEd | = | 1950 | kN |  | VEd is the applied shear force (max. pile reaction, vertical)
base area | = | 17351695 | mm2 |  | Unit wt. of concrete |  | 25 | KN/m3
within critical sec.
∆ VEd | = | 910.964 | kN |  | is the net upward force within the control perimeter considered
i.e upward pressure from soil minus self weight of base
Checking at pile perimeter
u0 | = | 1571 | mm |  | Perimeter of pile
vEd | = | VEd / u0 d
vEd | = | 0.59107 | N/mm2 | < | 3.5904 | N/mm2 | Ok, safe at pile perimeter
VRd,max
Checking at distance d from face of pile
u | = | 14767.4 | mm2 |  | u is the perimeter of the critical section considered
vEd | = | VEd,red / ud
vEd | = | 0.033505 | N/mm2 | < | 0.57395 | N/mm2 | Ok, no shear reinf. req.
(max of VRd and VRd,min)

## Crack Width
Crack width calculation
| Allowable crack width, wk1 |  |  |  | = |  | 0.3 | mm
As per clause 7.3.4
| fck |  |  |  |  | = | 30 | N/mm2
| fctm |  |  |  |  | = | 2.9 | N/mm2
| c= cover to reinforcement |  |  |  |  | = | 50 | mm
| K1 (for high bond bar) |  |  |  |  | = | 0.8
| K2 (for bending) |  |  |  |  | = | 0.5
| ᶲ = bar diameter |  |  |  |  | = | 20 | mm
| k |  |  |  |  | = | 0.01108
| Ac,eff = minimum of { 2.5 (h-d), (h-x)/3, h/2} x 1000 |  |  |  |  | = | 175000 | mm2
Depth of neutral axis, x = 2 (d-z) / λ
|  | x | = | 23.38 | mm
| here, h = D | h | = | 2170 | mm
| ρρeff | As / Ac,eff | = | 0.01796
Recommended values of k3 = 3.4 & k4 = 0.425 (pg no 126, EN 1992-3:2006)
| Sr,max | = 3.4 x50 + 0.8 x 0.5 x 0.425 x ( 20/0.01796) |  |  |  |  | = | 359.31
| Reinforcement Location | MU | K | d | z | As | Bar Dia
| Top X | 1464.58 | 0.01108 | 2100 | 2088.31 | 3142.8571 | 20 |  | 1464.58
| Top Y | 1449.425 | 0.01096 | 2100 | 2088.43 | 3142.8571 | 20 |  | -317.048
| Bottom X | 317.048 | 0.0024 | 2100 | 2097.48 | 3142.8571 | 20 |  | 1449.425
| Bottom Y | 1152.456 | 0.00872 | 2100 | 2090.81 | 3142.8571 | 20 |  | -1152.456
| Mu(max) | 1464.58
| σs = Mu/ (As x z) |  |  |  | = | 223.1483 | N/mm2
| αe = (2 x 105) / (33 x 103) |  |  |  | = | 6.06
(Refer table 3.1, EN 1991-1:20010-12)
| kt (for long term loading) |  |  |  | = | 0.4
| fct,eff = fctm |  |  |  | = | 2.9 | N/mm2
| ecr | = | εsm - εcm |  | = | 0.00075765
| Therefore, wk = Sr,max x ecr |  |  |  | = | 0.273 | mm
[6 empty] | < | wk1 | Safe

## One Way Shear (hidden)
yellow cells to be linked with main sheet
Check for one way shear
fck | = | 30 | Mpa
d | = | 2100 | mm (effective depth)
As per clause 6.2.2 (1) EN 1992-1-1 ed 11
The design value for the shear resistance VRd,c is given by
VRd,c | = CRd,c k (100 ᵨl fck)1/3 bw d |  |  |  | Refer EQ. 6.2.a (EN 1992 1-1)
with a minimum of
VRd,c MIN | = vmin bw d |  |  |  | Refer EQ. 6.2.b (EN 1992 1-1)
where
k | = | 1.3086 | ≤ 2
Bar dia | 20 | mm | at | 100 | mm c/c | (Refer Reinforcement calculation)
Asl | = | 3142.8571 | mm2
bw | is the smallest width of the c/s in the tensile area (mm)
bw | = | 1000 | mm
ᵨl | = | 0.0014 | ≤ 0.02
CRd,c | = | 0.18/γc |  |  | γc | = | 1.5 | (refer Table 2.1N, EN 1992-1-1)
CRd,c | = | 0.12 |  |  | Refer Cl. 6.2.2(1) note (EN 1992 1-1)(value to confirmed with National Annex)
vmin | = | 0.035 k3/2 fck1/2 |  |  | Refer EQ. 6.3N (EN 1992 1-1)
vmin | = | 0.286
VRd,c | = | 531.8 | kN
VRd,c MIN | = | 600.6 | kN
Strength reduction factor for concrete cracked in shear
Refer EQ. 6.6N (EN 1992 1-1)
v | = | 0.528
fcd | = | αcc fck / γc |  |  | Refer EQ. 3.15 (EN 1992 1-1)
αcc | = | 0.85 |  |  | Refer Cl. 3.1.6(1) note (EN 1992 1-1)(value to confirmed with National Annex)
fcd | = | 17
The design shear force VEd |  |  | = | 839.79 | kN
VEd | ≤ | (0.5bw d v fcd) |  |  | Refer EQ. 6.5 (EN 1992 1-1)
839.79 | ≤ | 9424.8 | kN
Also,
VEd | ≤ | VRd,c
839.79 | > | 600.6 |  |  | See shear reduction check
Shear reduction check
β | = | av/2d |  | For | av | = | d | Refer Clause 6.2.2(6) (EN 1992 1-1)
β | = | 0.5
β VEd | = | 419.895 | < | 600.6 |  |  | Hence safe

## SUMMARY
SUMMARY OF RAFT DESIGN
DIMENSIONS OF RAFT
LENGTH (L) = | 20.5 | m
BREADTH (B) = | 12 | m
THICKNESS (D) = | 2170 | mm
REINFORCEMENT DETAILS
Reinforcement Location | Ast reqd | Ast provided | Bar Diameter | Spacing | Remarks
Top X | 2444.5466 | 3142.8571 | 20 | 100 | O.K
Top Y | 2798.5433 | 3142.8571 | 20 | 100 | O.K
Bottom X | 1144.7913 | 3142.8571 | 20 | 100 | O.K
Bottom Y | 2683.3786 | 3142.8571 | 20 | 100 | O.K
CHECK FOR PUNCHING SHEAR
Actual Punching Shear stress (ved) | Allowable Punching shear stress (vRd) |  | Remarks
0.387 | 0.51786 |  | O.K
CHECK FOR CRACK WIDTH
Actual crack width (wk) | Allowable Crack Width (wk1) |  | Remarks
0.273 | 0.3 |  | O.K
CHECK FOR ONE WAY SHEAR
Actual Shear (β Ved) | Shear Capacity (min of VRd,c & VRd,c ) |  | Remarks
419.895 | 600.6 |  | O.K

## Pile Capacities
[9 empty] | 500 dia | 800 dia
[8 empty] | 3d | 225 | 555
Diameter of Pile Dp = |  |  |  | 500 | mm |  |  | 4d | 392 | 950
Length of Pile Lp = |  |  |  | 25 | m |  |  | >=6d | 510 | 1250
Type of Pile based on Connectors = |  |  |  | Type II | [5 empty] | 997
Pile group = |  |  |  | 3x3 Pile group |  |  |  | Area | Pile length | Compression capacity for 500 dia pile | Compression capacity for 800 dia pile | Tension capacity for 500 dia pile |  |  | Tension capacity for 800 dia pile
Pile Spacing = |  |  |  | >5D | [7 empty] | 3d | 4d | >=6d | 3d | 4d | >=6d
[8 empty] | I | 29 | 1950 | 4300 | 326.25 | 568.4 | 739.5 | 804.75 | 1377.5 | 1812.5
Pile group reduction factor = |  |  |  | 0 |  |  |  | II | 19.3 | 1846 | 4300 | 217.125 | 378.28 | 492.15 | 535.575 | 916.75 | 1206.25
[8 empty] | IIIa | 20.3 | 1950 | 4300 | 228.375 | 397.88 | 517.65 | 563.325 | 964.25 | 1268.75
Pile capacities as per PDE-CVC-G00-DD-0002 | [7 empty] | IIIb | 20 | 1950 | 4300 | 225 | 392 | 510 | 555 | 950 | 1250
[8 empty] | IV | 19.1 | 1950 | 4300 | 214.875 | 374.36 | 487.05 | 530.025 | 907.25 | 1193.75
Allowable compressive capacity = |  |  |  | 810 | kN | Ultimate capacity = | 1950 | V | 15 | 1950 | 4300 | 168.75 | 294 | 382.5 | 416.25 | 712.5 | 747.75
[8 empty] | VI | 21.3 | 1950 | 4300 | 239.625 | 417.48 | 543.15 | 591.075 | 1011.75 | 1061.805
Pile Settlement = |  |  |  | 0.39 | cm
Allowable Tensile capacity = |  |  |  | 621 | kN | Ultimate capacity = | 869.4
Allowable Shear capacity = |  |  |  | 63 | kN | Ultimate capacity = | 88.2
Spring constants : |  |  | Fy = | 207692.3077
|  |  | Fx = | 3150
|  |  | Fz = | 3150
Pile capacities as per PDE-CVC-G00-ED-0002
Pile-Pile cap bonding type II
Ultimate pile capacity in compression = |  |  |  | 1950 | kN
Corresponding ulitimate shear capacity = |  |  |  | 100 | kN
Ultimate pile capacity in tension = |  |  |  | 510 | kN
Corresponding ulitimate shear capacity = |  |  |  | 80 | kN
Relation between axial load & allowable shear load
| Ned (kN) | Hed (kN)
| 1950 | 100
| 520 | 80
| 250 | 60
| 0 | 42
| -100 | 35
| -200 | 25
| -400 | 14
| -510 | 6
Design compression capacity = |  |  |  | 1950 | kN
Design tension capacity = |  |  |  | 510 | kN |  | Actual Shear Capacity | Shear Capacity
[8 empty] | Axial | Shear
Actual compression = |  |  |  | 689.518 | kN |  |  | kN | kN
Design Shear capacity = |  |  |  | 82.3709 | kN |  | 82.3709 | -510 | 6
[8 empty] | -400 | 14
[8 empty] | -200 | 28
Actual tension = |  |  |  | -214.193 | kN |  |  | -100 | 35
Design Shear capacity = |  |  |  | 27.0065 | kN |  | 27.0065 | 0 | 42
[8 empty] | 250 | 60
[8 empty] | 520 | 80
vertical force = |  |  |  | 294.933 | kN |  |  | 1950 | 100
Design Shear capacity = |  |  |  | 63.3284 | kN |  | 63.3284 | Negative Value for Tension
vertical force = |  |  |  | 399.308 | kN
Design Shear capacity = |  |  |  | 71.0599 | kN |  | 71.0599

## Sheet1
DIA | TYPE A | TYPE B
16 | 337 | 340
20 | 440 | 443
24 | 450 | 450
30 | 457 | 461
36 | 566 | 570
42 | 575 | 580
48 | 585 | 590
56 | 700 | 805
64 | 810 | 815
72 | 820 | 825
80 | 845 | 845
90 | 950 | 960
100 | 970 | 980
Structural Class | Exposure Class according to Table 4.1
| XC4 | XD1 | XS1 | XF1 | XA1
S1 | 15 | 20 | 20 | 10 | 10
S2 | 20 | 25 | 25 | 10 | 10
S3 | 25 | 30 | 30 | 10 | 10
S4 | 30 | 35 | 35 | 10 | 10
S5 | 35 | 40 | 40 | 15 | 15
S6 | 40 | 45 | 45 | 20 | 20
C12/15 | 12
C20/25 | 20
C25/30 | 25
C30/37 | 30
C35/45 | 35
C40/50 | 40
C45/55 | 45
C50/60 | 50
C55/67 | 55
C60/75 | 60
C70/85 | 70
C80/95 | 80
C90/105 | 90
fck | εcu3 | fctm
12 | 0.0035 | 1.6
16 | 0.0035 | 1.9
20 | 0.0035 | 2.2
25 | 0.0035 | 2.6
30 | 0.0035 | 2.9
35 | 0.0035 | 3.2
40 | 0.0035 | 3.5
45 | 0.0035 | 3.8
50 | 0.0035 | 4.1
55 | 0.0031 | 4.2
60 | 0.0029 | 4.4
70 | 0.0027 | 4.6
80 | 0.0026 | 4.8
90 | 0.0026 | 5